## Heat Exchange Study
Double Pipe, Countercurrent, Aqueous, Heat Exchange Study
[9 empty] | 77 | °F
20
| 200 | °F |  |  |  |  | 10 |  |  |  | 86.9232 | °F
|  | 133.0065 | °F
[9 empty] | Area | Tube | Jacket
| Tube |  | QTube = F cp ( To - T ) | [5 empty] | 0 | 200 | 133.0065
10 | Process Flow, GPM |  |  |  |  | 4881.4066 | Process Flow, lbs/hr |  | 0.1 | 176.9242 | 121.5772
200 | Temperature In, °F |  |  |  |  | 86.9232 | Temperature Out, °F |  | 0.2 | 157.86 | 112.1347
1.094 | Viscosity, lb/ft-hr (1cp=2.42 lb/ft-hr) |  |  |  |  | 4.0847 | Velocity, ft/sec |  | 0.3 | 142.1101 | 104.3338
0.34729 | Thermal Conductivity, BTU/hr-ft²-°F/ft |  |  |  |  | 68173.8834 | Reynolds Number |  | 0.4 | 129.0981 | 97.8891
60.863 | Density, lbs/ft3 |  |  |  |  | 1733.0699 | Film Coefficient, BTU/hr-ft²-°F |  | 0.5 | 118.3482 | 92.5647
1 | Heat Capacity, BTU/lb-°F | [7 empty] | 0.6 | 109.4671 | 88.1659
[9 empty] | 0.7 | 102.13 | 84.5319
[9 empty] | 0.8 | 96.0683 | 81.5295
[9 empty] | 0.9 | 91.0605 | 79.0492
| Jacket |  | QJacket = C cpc ( Tc - Tco ) | [5 empty] | 1 | 86.9232 | 77
20 | Coolent Flow, GPM |  |  |  |  | 9855.5294 | Coolent Flow, lbs/hr
77 | Temperature In, °F |  |  |  |  | 133.0065 | Temperature Out, °F
1.5677 | Viscosity, lb/ft-hr (1cp=2.42 lb/ft-hr) |  |  |  |  | 2.7231 | Velocity, ft/sec
0.36306 | Thermal Conductivity, BTU/hr-ft²-°F/ft |  |  |  |  | 32016.8087 | Reynolds Number
61.441 | Density, lbs/ft3 |  |  |  |  | 1259.3073 | Film Coefficient, BTU/hr-ft²-°F
1 | Heat Capacity, BTU/lb-°F
| Exchanger |  |  |  |  | U = | 1
| QTube = | QJacket = | Q = U A (ΔT)lm |  |  |  | 1/ht + Δr/k + 1/hj
1 | Tube Diameter, in. (copper) |  |  | 26.1799 | Heat Exchanger Area, ft²
0.125 | Wall Thickness, in. |  |  | 705.5199 | Overall Heat Transfer Coefficient, BTU/hr-ft²-°F
100 | Tube Length, ft |  |  | 551973.7839 | Heat Load, BTU/hr
2 | Jacket Diameter, in. ft (steel) |  |  | 29.8841 | Log Mean Temperature Difference, °F
Inputs in Red | [7 empty] | Fluid Properties Calculated at Average Stream Temperature